# Engineering Specifications

# Veris H8035/H8036

# Networked Power Meters

- The power meter shall consist of three split-core CTs hinged at both axes with the power metering electronics embedded inside of the master CT.

- The meter shall measure true (RMS) power, instantaneous demand (kW) and consumption (kWh).

- The meter shall report kW/kWh serially over an RS-485 network using the Modbus (RTU) protocol.

- The consumption (kWh) variable shall be stored in non-volatile memory and retained in the event of a power outage.

- The meter shall directly accept any voltage input from 208-480 VAC.

- The meter shall be calibrated as a system and be accurate to +/- 1% from 10% to 100% of the rated current over a temperature range of 0-60 C.

- The meter shall conform to ANSI C12.1 metering standards.

- The power meter shall be internally isolated to 2000 VAC.

- The power meter case isolation shall be 600 VAC.

- The power meter available ordering ranges shall be 100-2400 Amps.

- The Power Meter shall be called Veris Industries model H8035 or H8036.